## Slide 1: KRYOLENS – Cryogenic Air Energy Storage ETIP SNET Regional Workshop
Aachen, 19.09.2017
Dr. Christian Bergins
Sven Bosser

## Slide 2: Kryolens – Project Overview
R&D project:
Timeline:
Partners:
Funding:
Financing:
Targets:
„Kryolens“ – Kryogene Luftenergiespeicherung (Cryogenic air energy storage)
October 1st 2016 until September 30th 2019
Mitsubishi Hitachi Power Systems Europe GmbH
Linde AG
Ruhr-University Bochum with the following chairs
  Energy plant technology (LEAT), Thermodynamics (TH),
  Thermal Turbomachines (TTM) and Energy systems and energy economics (LEE)
RWE Power AG
Uniper Technologies GmbH
Lausitzer Energie Kraftwerke AG (LEAG)
Federal Ministry for Economics Affairs and Energy (FKZ 03ET7068)
2,8 m€ overall project budget incl. 57 % net public funding and 4 %
external funding by LEAG, RWE and Uniper
Increase technology readiness level by process and component optimisation
as well as determination of the technology‘s techno-economic potential

## Slide 3: LAES (Liquid Air Energy Storage) - Principle & main advantages
store
discharge
charge
Liquid air storage
Expansion
Evaporation/ heating
Liquefaction
Cold-storage
Compression
Heat-storage
Pump
AIR
Electricity IN
Electricity OUT
External Heat
(OPTION)
AIR
No geologic limitations
No social and ecological issues
Flexibility and scalability
Efficiency up to 75%*
Based on mature technology
Realization time < 3 years
*Definition of efficiency, please see backup slides

## Slide 4: Mapping of Energy Storage Technologies
Chemical Storage

## Slide 5: Integration Capabilities of LAES
LAES
Peak shaving from RES to avoid curtailment
Ancillary services, Voltage support, energy trading, minimize grid expansion
District heating and cooling
Flexibilization of conventional power plants
Utilization of industrial waste heat, supply of cold, utilization and supply of pressurized air
Utilization of LNG regasification cold to avoid cold storage in LAES system

## Slide 6: Research Project - Content
Work packages |  |  | Lead | 16 | 2017 |  |  |  | 2018 |  |  |  | 2019 |  | 
 |  |  |  | Q4 | Q1 | Q2 | Q3 | Q4 | Q1 | Q2 | Q3 | Q4 | Q1 | Q2 | Q3
AP 1 | 1 | Project management | Linde | x | x | x | x | x | x | x | x | x | x | x | x
AP 2 Process analysis | 2.1 | Definition of applications and process variants | MHPSE | x | x |  |  |  |  |  |  |  |  |  | 
 | 2.2 | Technical boundary conditions and interfaces | MHPSE | x | x | x | x |  |  |  |  |  |  |  | 
 | 2.3 | Process analysis | LEAT | x | x | x | x | x | x | x | x | x | x | x | x
 | 2.4 | Operational behaviour | LEAT |  |  |  |  |  |  |  |  |  | x | x | x
AP 3 Component analysis | 3.1 | Hot plant section | MHPSE | x | x | x | x | x | x | x | x | x | x | x | x
 | 3.2 | Cold plant section | Linde | x | x | x | x | x | x | x | x | x | x | x | x
 | 3.3 | Turbomachinery | TTM | x | x | x | x | x | x | x | x | x | x | x | x
 | 3.4 | Thermal Storage | TH | x | x | x | x | x | x | x | x | x | x | x | x
AP 4 Economic analysis | 4.1 | Analysis of plant specific data and boundary conditions of energy economics | LEE | x | x | x | x | x | x | x | x | x | x | x | 
 | 4.2 | Economic analysis | LEE |  | x | x | x | x | x | x | x | x | x | x | x
 | 4.3 | Life Cycle Approach | LEE | x | x | x | x | x | x | x | x | x | x | x | X
Milestones
MS 1 State of the art imaged; Most promising markets defined; Revenue potential of SOTA determined
MS 2 Preferred process variants defined; First economic assessment finished; Technical potential of core components defined; Process calculation for basis processes finished; Design and order of cold storage test facility finished
MS 3 Conceptual design of core components finished; Experimental investigations finished
MS 4 Balance of plant and operational behaviour analysed; Economic assessment finished; Overall assessment available
MS 1
MS 2
MS 3
MS 4
today
Process design
Component design
Economics and Life Cycle Approach

## Slide 7: AP 2: Process Analysis Definition of preferred Process Variants – Flex-LAES
G
M
LP Pre-Heating Bypass
m const.
.
Power in
Power out
LAES Charging
LAES Discharging
(coal-fired) Power Plant
Air heating with steam (PP max. load / LAES discharging)
Compression heat for feed-water pre-heating (PP min. load / LAES charging)
HP Pre-Heating
LAIR Storage
Cold Storage
Priority 1: Flex-LAES
Flexibilisation of existing and new power plant
Time shifted power generation
Peak power supply

## Slide 8: Flex-LAES: Efficiency & Load Range for PCPP + LAES
0,5
0,4
0,3
0,2
0,1
0 200 400 600 800 900
P
Net
[MW]
Steam Cycle
Reduced minimum Load of PCPP
Additional power in combined operation of PCPP and LAES system
Time Shifted Power Generation
Combined Powering PCPP + LAES

## Slide 9: AP 2: Process Analysis Definition of preferred Process Variants – A-LAES
Power in
Power out
G
Heat storage
Cold storage
Lique- faction
Evapo-rator
Liquid air
Multi-stage air expander
Exh. air
Intercooled air-compression
Liquid air pump
Priority 2: Adiabatic-LAES
Power-to-Power storage
No external heat or fuel use
Comparability with batteries

## Slide 10: AP 2: Process Analysis Definition of preferred Process Variants – Fuel-LAES
Power out
Power out
HRAH
G
G
Intercooled air-compression
Air expander
Natural gas In
Liq. air pump
Cold storage
Lique- faction
Evapo-rator
Liquid air
Fluegas out
Power in
Air in
Priority 3: Fuel-LAES
Hybrid storage (with fuel use)
High efficiency and energy density
Development of turbomaschinery (derived from GT)

## Slide 11: AP 2: Process Analysis Definition of preferred Process Variants – Industry-LAES
Priority 4: Industry-LAES / LNG-LAES
High potential of efficieny increase (use of waste heat and cold)
LNG cold could replace cold storage
Limited availability of heat and cold
Not site independent
Power in
Power out
G
Heat storage (optional)
External heat from industrial process
Intercooled air-compression
Multi-stage air expander
Exh. air
Liq. air pump
Cold storage
Lique- faction
Evapo-rator
Liquid air
External cold from LNG regasification

## Slide 12: Keynotes
Main lessons learned and barriers to innovation deployment:
  Flexibility of Flex-LAES (start-up time) need to be increased because fast reacting short term storage is most important for power plant utilities
  Solid bed cold storage can significantly increase the efficiency of the process
  Cost reduction necessary to compete with alternative storage technologies
The next project steps:
  Identification of most relevant process sub-variants
  Detailed component design for Flex-LAES and A-LAES
  Identify cost reduction potential
Needs for future R&I activities coming out of the project:
  Small scale pilot plant to prove technical feasibility
Deployment prospects of the most promising solutions.
  Flex-LAES to improve flexibility of power plants in Western Europe (hard coal and lignite)
  A-LAES as alternative to large scale batteries in island grids

## Slide 15
Backup Slides

## Slide 16: AP 2: Process Analysis Process calculations of Flex-LAES and A-LAES (LEAT)
Reference power plant for thermal calculations of Flex-LAES process is conceptual study of the reference power plant NRW (RKW NRW) from 2004
Investigation of different integration points (charging and discharging)
 2 process variants defined for detailed analysis
Different heat transfer fluids and heat storage fluids under investigation for A-LAES
7 process variants identified for further investigation
Influence of different heat transfer fluids on efficiency of A-LAES process:
Discharging pressure

## Slide 17: AP 3: Component Analysis Hot plant section – heat exchanger (MHPSE)
Design, construction and arrangement planning for heat exchanger of the hot plant section
Example:
arrangement planning for
A-LAES gas liquid heat exchanger
Modular construction  quick adjustment to size requirements
Optimisation of component parameters and materials for cost reduction and efficiency improvement

## Slide 18: AP 3: Component Analysis Storage Materials for Packed Bed Cold Storages (RUB–TH)
Storage mass and cylinder volume
  Material price, storage mass and cylinder volume are economic indicators of the packed bed cold storage
Analysis of storage efficiency and material properties:
Analysis of storage materials
  Nine materials are investigated
  Lead yields the best storage efficiency η
  PP, PE, NaCl and quartz yield the best compromise of feasibility and economy

## Slide 19: AP 3: Component Analysis Market Screening for adiabatic Compressors for A-LAES (TTM)
Compression end temperature of 350°C with state of the art compressors available
Higher temperatures up to 625°C (aero derivative gas turbines with π=34) by using axial compressors and gas turbine technology (high temperature materials)
source: Siemens AG
Example: adiabatic axial compressor (Siemens) with Tmax,compression = 350 °C
Example: Aero derivative gas turbine GE LMS 6000 with Tmax,compression = 625 °C
source: General Electric

## Slide 20: AP 4: Economic Analysis Benchmark PV+A-LAES vs. CSP+TES and Life Cycle Approach (LEE)
Investigation of CSP+TES projects woldwide for definition of: techno-economic parameters of CSP plants
Definition of A-LAES size (input for process and component analysis AP2/AP3): 50MW, 350MWh
Investigation of relevant CSP and PV markets
Definition of suitable CSP projects for benchmark dependent on: technical parameters, market attractiveness and solar radiation
consideration of whole life cycle (manufacturing, use phase, disposal)
Comparison of resources and emissions with other storage technologies and power plants
source: J. Röder

## Slide 21: Advantages of LAES
Based on mature technology
No geologic limitations
No social & ecological issues
Realization time < 3 years
Flexibility, scalability
Efficiency of up to 75 %
Long lifetime
Liquid Air Energy Storage

## Slide 22: Known ES technologies face severe limitations – A one-fits-all solution is out of sight
Batteries
  Limited lifetime
  High storage capacity costs
  Disposal
Pumped Hydro
  Need mountains
  Social, environ-mental issues
  Long realization time
Flywheels,
Capacitors
  Short duration of storage
  High storage capacity costs
Compressed Air
  Need salt dome
  Long realization time

## Slide 23: LAES – Fact Sheet
  Energy Density: 70 – 100 kWh/m3
  Power output: 10 – 600 MW
  Storage Capacity: > 1000 MWh
  Discharging duration: 2 – 12 h
  Efficiency: 50 – 65 %
  (>65 % by utilizing waste heat)
  Lifetime: 20 – 30 years
Pictures:
1) 3D plot of LAES power recovery unit (MHPSE)
2) Cryogenic storage tank 1600 m3 (Source: The Linde Group)
Storage Density [kWhel/m³]
100-500m, hSp~70-85%
50bar, hSp~50-65%
hSp~50-65%
50-100 bar
hGuD=60%
0,1
1
10
100
PHS
CAES
LAES
SNG

## Slide 24: LAES - Comparison to CAES
 | Huntorf CAES | McIntosh CAES | GT-LAES Technology (4h dis.) (H25(32) / H80 / M501JAC)
Capacity, MWh | 480 | 1060 | 304 / 1004 / 2564 *
Power-Output, MW | 321 | 110 | 76 / 251 / 641 *
Round trip efficiency, % | 42 | 54 | 52 / 54 / 56
Storage volume, m3 | 310 000 | 538 000 | 1 900 / 6 000 / 11 300 **
Storage density, kWh/m³ | 1.55 | 1.97 | 160 / 167 / 227
Source: The Linde Group
CAES
LAES
Time-factor (Charging-/Discharging-time): Huntorf 4 / McIntosh 1.6 / LAES 2 (variable)
* GT power incl.
** LAIR

## Slide 25: GT-LAES – Stand-alone or Retrofit based on mature Components
Power out
Power out
Air expander
Fluegas out
Natural gas In
Intercooled air-compression
Exh. air
Air in
Lique- faction
Liquid air
Cold storage
Evapo-rator
G
G
Power in
Liq. air pump
approx. 10 - 200 MWel
Storage Input:
Storage Output (Air expander):
approx. 10 - 300 MWel
Heat recovery air heater
Efficiency:
ηsystem = 81 – 83 % ηs,50% = 55 – 67 %
ηRT = 52 – 56 %
ηF = 83 – 86 %
mCO2 < 240 kg/MWhel
 GT-LAES combines energy storage with GT peaker plant
Gas turbine (new or retrofit)

## Slide 26: CO2-Footprint of produced Electricity OCGT / CCGT / LAES
OCGT
CCGT
GT-LAES
adiabatic LAES
(future outlook)
[kgCO2/MWhel]
0
~526
~345
~230
*

## Slide 27: LAES Efficiency
System Efficiency:
ηsystem =
Storage Efficiency:
ηs,NG% =
Round-trip Efficiency:
ηRT =
Fuel Efficiency:
ηF =